## Data
Feasibility Study - Rooftop Solar Power Plant
Investor: |  |  |  |  | Date: | 14.09.2025
Design company: |  |  |  |  | Google coordinates: | 44.88032, 20.47319
INPUT DATA
INPUT DATA PER ROOF
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Tilt angle [°] | 30.0° | 30.0° | 30.0° | / | / | / | / | / | / | /
Azimuth angle [°] | 27.0° | 27.0° | 26.0° | / | / | / | / | / | / | /
Free surface [m²] | 34.82m² | 28.88m² | 53.35m² | / | / | / | / | / | / | /
Energy consumption |  |  |  |  | PV module information
Annual electricity consumption [kWh] | 25000 kWh |  |  |  | Nominal power [Wp]: |  | 585.0 Wp |  | Note: Additional safety space on the roofs will be included in the calculations
Share of higher tariff in electricity consumption [%] | 80.0 % |  |  |  | Length [mm]: |  | 2278 mm
[5 empty] | Width [mm]: |  | 1134 mm
OUTPUT DATA
Recommended power of the PV power plant [kWp] |  | 16,38 kWp |  | Total energy savings in the exploitation period [kWh] |  |  |  | 526.724,29 kWh
Maximum power that can be installed on the roofs [kWp] |  | 21,64 kWp |  | CO2 emissions reduction during the exploitation period [tons] |  |  |  | 474,33 tons
Total estimated annual energy production [kWh] |  | 20.413,65 kWh |  | Estimated annual maintenance costs [EUR] |  |  |  | 196,56 EUR
Total used area of ​​the roofs [m²] |  | 83,18 m² |  | Estimated value of the investment [EUR] |  |  |  | 9.828 EUR
Annual energy savings [kWh] |  | 20.000,00 kWh |  | ROI [years] |  |  |  | 3,71 years
Annual energy savings [EUR] |  | 2.696,32 EUR
OUTPUT DATA PER ROOF Note: The roofs are sorted by optimality for use
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Roof tilt angle [°] |  | 30 ° | 30 ° | / | / | / | / | / | / | / | /
Roof azimuth angle [°] |  | 26 ° | 27 ° | / | / | / | / | / | / | / | /
Power that can be installed on the roof [kWp] |  | 9,95 kWp | 6,43 kWp | / | / | / | / | / | / | / | /
Number of PV modules per roof |  | 17 | 11 | / | / | / | / | / | / | / | /
Estimated annual energy production per roof [kWh] |  | 12.400,92 kWh | 8.012,73 kWh | / | / | / | / | / | / | / | /
Used roof area [m²] |  | 50,50m² | 32,68m² | / | / | / | / | / | / | / | /
Feasibility Study - Rooftop Solar Power Plant
MONTHLY ENERGY DATA [kWh]
Month | Production
January | 857.025
February | 1092.9614
March | 1730.6055
April | 2008.8256
May | 2219.9873
June | 2290.3861
Jully | 2528.2823
August | 2372.4266
September | 1895.9441
October | 1601.7651
November | 1069.772
December | 745.6703
TOTAL | 20.414 kWh | 3: Note: Calculations were made on an hourly basis during the year
CASH FLOW |  | 8: EQUIPMENT RECOMMENDATION
Year | Status [EUR]
2024 | -7131.68 | 8: DC cables lenght [m]; 10: 295 m
| -4489.29 | 8: Mounting system type - example; 10: K2 SolidRail System
-1861.43
| 751.98 | 8: PV modules
| 3351.01 | 8: Nominal power [Wp]; 10: Quantity
| 5935.75 | 8: 585 Wp; 10: 28
8506.28
| 11062.66 | 8: Inverters
| 13604.99 | 8: Nominal power [kW]; 10: Quantity
| 16133.33 | 8: 17; 10: 1
18647.76
21148.37
23635.22
26108.4
28567.97
| 31014.02 | 8: Note: This is an equipment recommendation based on basic calculations. Consultation with an expert to check the adequacy of the equipment is recommended.
33446.61
35865.82
38271.73
40664.41
43043.92
45410.35
47763.76
50104.23
52431.83
54746.62
57048.68
59338.08
61614.89
63879.18