## Data
Feasibility Study - Rooftop Solar Power Plant
Investor: |  |  |  |  | Date: | 23.09.2025
Design company: |  |  |  |  | Google coordinates: | 44.72978, 20.03211
INPUT DATA
INPUT DATA PER ROOF
Roof number | 1 | / | / | / | / | / | / | / | / | /
Tilt angle [°] | 35.0° | / | / | / | / | / | / | / | / | /
Azimuth angle [°] | 70.0° | / | / | / | / | / | / | / | / | /
Free surface [m²] | 150.0m² | / | / | / | / | / | / | / | / | /
Monthly energy consumption in the high tariff [kWh] |  |  |  |  | Electricity prices
January | 5000.0 kWh |  |  |  | Base price of electricity [EUR/MWh]: |  | 120 EUR / MWh
February | 4000.0 kWh |  |  |  | Taxes and VAT [% of electricity price]: |  | 30.0 %
March | 3200.0 kWh |  |  |  | Total electricity price [EUR/MWh]: |  | 156.0 EUR / MWh
April | 4000.0 kWh |  |  |  | Selling price of electricity [EUR/MWh]: |  | 115 EUR / MWh
May | 4600.0 kWh
June | 7000.0 kWh |  |  |  | PV module information
Jully | 5300.0 kWh |  |  |  | Nominal power [Wp]: |  | 460.0 Wp |  | Note: Additional safety space on the roofs will be included in the calculations
August | 5450.0 kWh |  |  |  | Length [mm]: |  | 1800 mm
September | 7500.0 kWh |  |  |  | Width [mm]: |  | 1134 mm
October | 7450.0 kWh
November | 3000.0 kWh
December | 6000.0 kWh
Maximum authorised power [kW]: | 30.0 kW
OUTPUT DATA
Recommended power based on the electricity consumption [kWp] |  | 47,38 kWp |  | Total energy savings in the exploitation period [kWh] |  |  |  | 758.899,89 kWh
Maximum power based on the free roof surface [kWp] |  | 28,98 kWp |  |  | Annual energy surplus [kWh] |  |  | 3.971,90 kWh
Final power of the PV plant [kWp] |  | 28,98 kWp |  |  | Annual energy surplus [%] |  |  | 12,52 %
Total estimated annual energy production [kWh] |  | 31.733,60 kWh |  |  | Total energy surplus in the exploitation period [kWh] |  |  | 108.576,61 kWh
Total used area of |  | 147,88 m² |  |  | CO2 emissions reduction during the exploitation period [tons] |  |  | 737,36 tons
Annual energy savings [kWh] |  | 27.761,70 kWh |  |  | Estimated annual maintenance costs [EUR] |  |  | 579,60 EUR
Annual energy savings [%] |  | 44,42% |  |  | Estimated value of the investment [EUR] |  |  | 28.980 EUR
Annual energy savings [EUR] |  | 4.787,59 EUR |  |  | ROI [years] |  |  | 6,22 years
Feasibility Study - Rooftop Solar Power Plant
OUTPUT DATA PER ROOF Note: The roofs are sorted by optimality for use
Roof number |  | 1 | / | / | / | / | / | / | / | / | /
Roof tilt angle [°] |  | 35 ° | / | / | / | / | / | / | / | / | /
Roof azimuth angle [°] |  | 70 ° | / | / | / | / | / | / | / | / | /
Power that can be installed on the roof [kWp] |  | 28,98 kWp | / | / | / | / | / | / | / | / | /
Number of PV modules per roof |  | 63 | / | / | / | / | / | / | / | / | /
Estimated annual energy production per roof [kWh] |  | 1.095.017,25 kWh | / | / | / | / | / | / | / | / | /
Used roof area [m²] |  | 147,88m² | / | / | / | / | / | / | / | / | /
MONTHLY ENERGY DATA
Month | Consumption | Production | Surplus | Savings | Monthly expenses in HT with a PV power plant | Monthly expenses in HT without a PV power plant
January | 5.000 | 1.134 | 20 | 1.114 | 780 | 604
February | 4.000 | 1.565 | 144 | 1.421 | 624 | 386
March | 3.200 | 2.430 | 688 | 1.742 | 499 | 148
April | 4.000 | 3.289 | 713 | 2.576 | 624 | 140
May | 4.600 | 3.658 | 665 | 2.993 | 718 | 175
June | 7.000 | 3.879 | 314 | 3.565 | 1.092 | 500
Jully | 5.300 | 4.519 | 496 | 4.022 | 827 | 142
August | 5.450 | 3.729 | 302 | 3.427 | 850 | 281
September | 7.500 | 2.786 | 157 | 2.629 | 1.170 | 742
October | 7.450 | 1.970 | 111 | 1.859 | 1.162 | 859
November | 3.000 | 1.682 | 338 | 1.344 | 468 | 219
December | 6.000 | 1.094 | 23 | 1.072 | 936 | 766
TOTAL | 62.500 | 31.734 | 3.972 | 27.762 | 9.750 | 4.962 | Note: Calculations were made on an hourly basis during the year
CASH FLOW | [8 empty] | EQUIPMENT RECOMMENDATION
Year | Status [EUR]
2026 | -24192.41 | [7 empty] | DC cables lenght [m] |  | 522 m
| -19500.56 | [7 empty] | Mounting system type - example |  | K2 SolidRail System
-14834.53
| -10194.15 | [7 empty] | PV modules
| -5579.3 | [7 empty] | Nominal power [Wp] |  | Quantity
| -989.83 | [7 empty] | 460 Wp |  | 63
3574.4
| 8113.52 | [7 empty] | Inverters
| 12627.68 | [7 empty] | Nominal power [kW] |  | Quantity
| 17117.01 | [7 empty] | 20 |  | 1
21581.65
26021.74
30437.4
34828.78
39196
| 43539.21 | [7 empty] | Note: This is an equipment recommendation based on basic calculations. Consultation with an expert to check the adequacy of the equipment is recommended.
47858.53
52154.09
56426.03
60674.47
64899.54
69101.38
73280.1
77435.85
81568.73
85678.89
89766.44
93831.51
97874.22
101894.69